Basic Concepts of IEC 61499

James H. Christensen

ABSTRACT: This paper describes the history, basic concepts and current status of the IEC 61499 standard for the application of function blocks in distributed industrial-process measurement and control systems.  The means by which the draft standard addresses key issues in execution scheduling, communication/execution interaction, state machine design and system agility are discussed in sufficient detail to permit an understanding of the rationale for its major features.

# KEYWORDS: function blocks, IEC 61499, distributed control, real-time, event-driven

## History

In early 1990, Technical Committee 65 of the International Electrotechnical Commission (IEC TC65) received a New Work Proposal (NWP) to standardize certain aspects of the application of software modules called function blocks in distributed industrial-process measurement and control systems (IPMCS).  IPMCSs utilizing the "fieldbus" (IEC 61158) standard then in development in Working Group 6 of Subcommittee 65C (SC65C/WG6) were especially emphasized in the NWP.  However, function blocks were also an essential part of the programming language standard IEC 61131-3 for programmable controllers being developed in SC65B/WG7. Therefore, TC65 determined that a common model for the use of function blocks was required and assigned the new Project 61499 to a new Working Group 6 (TC65/WG6) of the parent committee.

Due to the relative immaturity of the IEC 61158 project at the time of the proposal, Experts and a Project Leader were not available for the 61499 project until approximately two years after its inception, at which time the first edition of IEC 61131-3 was also completed and available for reference.

In its first meetings TC65/WG6 identified a number of fundamental issues which had to be resolved in order to achieve a common model for the application of function blocks in distributed IPMCSs.  Through a long process of systematic application of software engineering and open systems principles, with intensive international review and revision, a consensus has emerged on the basic concepts and detailed technical approach to the resolution of these issues.

## Fundamental issues

The major challenges in evolving the application of function blocks from classical PLCs to distributed IPMCSs is apparent from comparison of Figures 1 and 2(a)-(c) below.  In Figure 1, function blocks are considered to be elements of programs in a centralized controller. In Figure 2 they are considered to be elements of distributed applications in a decentralized control system as envisioned in IEC Project 61804 by Experts of SC65C/WG7.  These examples illustrate the following fundamental issues that must be addressed in a generally applicable model for the use of function blocks in distributed IPMCSs:

- Execution scheduling: As shown in Figure 1, in an IEC 61131-3 configuration the execution of a program is triggered by a periodic or non-periodic task.  Upon triggering, the function block instances in the program are executed in a predetermined order.  Similarly, as shown in Figure 2(c), execution of function block instances in a distributed system may be performed according to a predetermined cyclic schedule.  However, IEC 61499 must support a more generalized model in which a centralized mechanism for enforcing execution schedules may or may not exist.

- Communication/execution interaction: As illustrated in Figure 1, in the IEC 61131-3 model communication and I/O functions are only loosely coupled to variables used in programs through the "access path" and "global and directly represented variable" mechanisms. Also, within programs a fixed order of function block execution can be determined such that new values of variables are available before beginning the execution of a function block which uses them.  However, as illustrated in Figures 2(b) and 2(c), in a distributed careful consideration needs to be given to the relationships among sampling of I/O data, execution of control algorithms contained in function block bodies, and communication of data among devices.  Again, these relationships must be explicitly expressible and manageable in systems, which may not have centralized scheduling mechanisms available.

Figure 1 – Function Blocks (FB) in the IEC 61131-3 configuration model

Figure 2(a) – Physical layout of a decentralized IPMCS

- Response time requirements: In all control systems, control cannot be maintained unless constraints are satisfied among the times of occurrence of changes an input variables and the time at which corresponding corrective actions are effected at appropriate output variable(s). In a centralized control system as in the 61131-3 model, these constraints are usually met either (a) by assuring that input and output sampling and program execution are always faster than necessary, e.g., to exceed Nyquist sampling criteria by a substantial margin; or (b) by careful fine-grained partitioning and scheduling of I/O sampling and program execution.  In a distributed system, similar criteria must be met without necessarily having the luxury of a centralized scheduling mechanism.  In addition, the IEC 61499 model must accommodate the enhanced performance made possible by using priority-based communications as in CAN networks, or by using unscheduled high-speed links such as Ethernet.

Figure 2(b) – Structure of a distributed applicationError: Reference source not found

- Alternative algorithm selection: A generic function block model should accommodate the existence of multiple alternative algorithms within a single function block body, selectable depending on some external event or condition, e.g., initialization algorithms, normal operation algorithms or fault processing/recovery algorithms.

- State machine design: High-speed, event-driven state machine control is essential to many modern machine control applications, as contrasted to the slower execution time requirements typical of many process control applications.  A general function block model for distributed IPMCSs must accommodate both sets of requirements.

- Software encapsulation and reuse: Encapsulation and reuse of control algorithms by end users, equipment suppliers and system integrators is much more widespread in manufacturing operations typically addressed by the IEC 61131-3 programming languages than in process control operations.  The need for this capability will persist and even become more widespread as manufacturing control becomes more distributed.

- Agility: Industrial processes of the future will exhibit much higher degrees of physical reconfigurability in order to accommodate frequent changes in product mix and volume, as well as the frequent introduction of new product types and manufacturing technology.  In addition, rapid reconfiguration of the industrial process will be used much more frequently to recover from machine and process faults with minimal loss of production.  In all these cases, the control system must be reconfigured quickly and for the most part automatically in order not to become a bottleneck to agility.  In fact, in the not too distant future it is anticipated that control systems for autonomous, intelligent manufacturing units ("holons") will be required to be intelligently self-reconfiguring in order to accomplish task assignments arrived at through negotiation with other holons.  This will further increase requirements for software encapsulation and reuse as well.

| Block Tag | Scheduled Block Execution |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| LT101 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| FT102 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| FIC102 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| IP102 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| FRC103 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SC103 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| AT103 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| AY103 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| AT106 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| AIC106 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| AT107A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| AT107B |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| HS107 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| AIC107 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tag/Parameter | Scheduled Communication |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| AT107A/OUT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| FIC102/OUT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| FRC103/BKCAL_OUT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| IP102/BKCAL_OUT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| AIC106/BKCAL_OUT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| AY103/OUT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| AIC107/OUT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| AIC106/OUT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| FT102/OUT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Devices | Time Available for Acyclic Communications |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| All |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Figure 2(c) – Communication/Execution Interleaving

## Basic concepts

- Distributed applications: Figure 3 illustrates the general concept of a distributed system in IEC 61499, in which devices may communicate with each other over one or more communication links, and may interface to controlled machines and processes; this can be recognized as an abstract model of the type of system shown in Figure 2(a).  Applications may be distributed among one or more devices.  As shown in Figure 4, an application consists of one or more function block instances, interconnected by event connections and data connections.  The function block instances may be distributed among devices.  Again, this can be recognized as an abstract model of the type of application shown in Figure 2(b), with the addition of event connections for more generalized execution control, as discussed below.

For consistency with the IEC 61131-3 model, and with the concept of multiple "virtual devices" within a "physical device", a device can be further subdivided into resources which then contain the function blocks used within the application as well as service interface function blocks for performing I/O, communication and other services provided by the resource's operating system, as illustrated in Figure 5.

Figure 3 – Distributed system concept

Figure 4 – A distributable applicationError: Reference source not found

- Event and data interfaces: In IEC 61499, function blocks are considered to be instances of function block types.  IEC 61499 provides both graphical and textual means for the declaration of the event and data interfaces of a function block type, and for the association of data inputs and outputs with event inputs and outputs, as illustrated in Figure 6.  In practice, the data types and data type extension mechanisms defined in IEC 61131-3 have been found adequate for the declaration of data interfaces.

- Event-driven state machine control of execution: As shown in Figure 7, in IEC 61499 basic function block types are defined by declaring: (1) their external interfaces as shown in Figure 6; (2) their Execution Control Chart (ECC); and (3) the algorithms whose execution may be invoked by the ECC.  The ECC may be considered a specialized version of the Sequential Function Chart (SFC) defined in IEC 61131-3, where EC transition conditions may be expressed as combinations of event inputs and other Boolean conditions.  One or more EC actions associated with an EC state specify the algorithm(s) to be executed upon entering the EC state and the output event(s) to be issued upon completion of algorithm execution.  The algorithms themselves may be expressed in the programming languages defined in IEC 61131-3 or other languages, utilizing the values of input, output and internal variables to produce new values of internal and output variables.

Figure 5 – A resourceError: Reference source not found

Figure 6 – Function block interface declarations

|  | (b) |
| --- | --- |

Figure 7 – Event-driven execution control
(a) A basic function block type; (b) An Execution Control Chart (ECC)

- Service interfaces: This function block type was initially defined in order to provide interfaces to communication services which are well-specified as sequences of service primitives as defined in ISO TR8509, since service primitives could be mapped directly to event inputs and outputs of service interface function blocks (SIFBs).  However, it was discovered that the SIFB concept applied equally well to process I/O and other operating system services such as timing and clock generation.  An example of SIFBs for the transmission of data items over a communication link is shown in Figure 8.  See IEC 61499-1 for additional extensive details.

Figure 8 – Typical service interface function block (SIFB) interfaces and service sequences

- Management services: The service interface function block (SIFB) concept was found to apply equally well to services for application management such as function block creation, deletion, interconnection and activation.  Such services are expected to increase in importance along with the demand for system agility.  An illustration of a communication function block interconnected with a management function block to provide remote application management services is presented in Figure 9.

Figure 9 – An example of remote management service provision
(not all details shown)

- Software encapsulation and reuse: IEC 61499 meets these requirements very well. Encapsulation is provided for algorithms written in the IEC 61131-3 languages or others in basic function block types.  Additionally, encapsulation of IEC 61499 function block networks themselves is provided in composite function block types and subapplication types as well.  See IEC 61499-1 for additional details.

- Software portability: The ability to utilize heterogeneous software environments, with software tools available from a wide selection of vendors, will be as essential to the early adoption and widespread use of IEC 61499 as the availability of a wide selection of interoperable, IEC 61499-compliant devices.  To this end, IEC 61499-2 provides XML DTDs (Document Type Definitions) for the standardized exchange of all IEC 61499 software library elements, including data types, function block types, adapter and subapplication types (not discussed in this paper), device and resource types and system configurations.

## The future of IEC 61499

Recognizing the need for an interim period for experimental applications of IEC 61499 before its finalization as an International Standard, the Advisory Group of IEC 61499 has accepted the recommendation of TC65/WG6 that the contents of IEC 61499-1 and –2 be "frozen" for a period of approximately two years.  This will take place as soon as National Committee comments on the previous draft of IEC 61499-1 and the currently pending draft of IEC 61499-2 are incorporated, probably by the middle of this year.  It is anticipated that these "frozen" drafts will take the form of "Publicly Available Specifications (PAS)", which will be the first trial of the use of this mechanism to provide a trial implementation period for pending standards.

A large amount of experimental work and trial implementations is expected to result in final standards of high technical quality and broad international consensus to be issued in approximately mid-2003.

Senior Principal Engineer, Rockwell Automation Advanced Technology, 24800 Tungsten Road, Euclid OH 44117 USA, E-mail: JHChristensen@ra.rockwell.com

T.Blevins, Example of Cyclically Scheduled Function Blocks, IEC SC65C/WG7, London, Oct. 21-23, 1996.

See, for example, http:// hms.ifw.uni-hannover.de/

IEC 65/240/CD, Function blocks for industrial-process measurement and control systems - Part 1: Architecture, 2 June 1999.

ISO TR 8509-1987, Information processing systems - Open Systems Interconnection - Service conventions

See http://www.w3.org/TR/1998/REC-xml-19980210